## survey
type | name | label | repeat_count | hint | constraint | constraint_message | required | appearance | default | relevant | read_only | calculation | hint::spanish | label::spanish
begin group | data
string | collectionMethod | Method | [7 empty] | 1=2 | yes | ODK
deviceid | deviceID
start | timeStarted
end | timeFinished
select_one plants | plant | Plant Name |  | Which plant are you working at? |  |  | yes | [6 empty] | ¿En cuál planta trabaja?
calculate | nFilters | [10 empty] | pulldata('nFilters', 'n', 'plantName_key', ${plant})
select_multiple purposes | purpose | What do you want to do? | [11 empty] | ¿Qué quiere hacer?
begin group | plantData | Plant Data | [7 empty] | selected(${purpose}, 'plantData') |  |  |  | Datos sobre la planta
dateTime | timeCollected | When did you collect this data? |  |  |  |  | yes | [6 empty] | ¿Cuándo recogió los datos?
decimal | flowRate | Flow Rate (Liters per second L/s) |  |  |  |  | yes | [6 empty] | Caudal (L/s)
integer | CDCPos | CDC Slider Position |  |  |  |  | yes | [5 empty] | (valor de 0-100 indicado en la ventanita del deslizador) | Posición del deslizador de coagulante en la balanza
decimal | rawWaterTurbidity | Raw Water Turbidity (NTU) |  |  |  |  | yes | [6 empty] | Turbiedad de agua cruda (NTU)
decimal | settledWaterTurbidity | Settled Water Turbidity (NTU) |  |  |  |  | yes | [6 empty] | Turbiedad de agua decantada (NTU)
acknowledge | setlledWaterTurbidityCheck | The SETTLED WATER TURBIDITY you have entered is outside the expected range (0.0-20.0). Please GO BACK to change your entry, or SELECT OK to save and continue. | [7 empty] | ${settledWaterTurbidity} >= 20 |  |  |  | El valor de TURBIEDAD DE AGUA DECANTADA que ha entrado cae fuera del rango esperado (0.0-20.0). Por favor, VOLVER para cambiar el dato, o SELECCIONAR OK para guardarlo y seguir.
decimal | filteredWaterTurbidity | Filtered Water Turbidity (NTU) |  |  |  |  | yes | [6 empty] | Turbiedad de agua filtrada (NTU)
acknowledge | filteredWaterTurbidityCheck | The FILTERED WATER TURBIDITY you have entered is outside the expected range (0.0-5.0). Please GO BACK to change your entry, or SELECT OK to save and continue. | [7 empty] | ${filteredWaterTurbidity} >= 5 |  |  |  | El valor de TURBIEDAD DE AGUA FILTRADA que ha entrado cae fuera del rango esperado (0.0-5.0). Por favor, VOLVER para cambiar el dato, o SELECCIONAR OK para guardarlo y seguir.
decimal | coagDoseSuggestion | Coagulant Dose Suggestion (mg/L) |  | This requires having downloaded the app "POST dose". |  |  | no | ex:org.post.aguaclara.postdose.COLLECT(rawWaterTurbidity=${rawWaterTurbidity},plantName=${plant}) | [5 empty] | Esto requiere haber descargado la aplicación "POST dose". Dosis de coagulantes SUGERIDA (mg/L)
decimal | coagulantDose | Coagulant Dose (mg/L) |  | Ensure that all but one of the dosage tubes are open |  |  | yes | [6 empty] | Dosis de coagulantes (mg/L)
acknowledge | coagulantCheck | The COAGULENT dose you have entered is outside the expected range (0.0-50.0). Please GO BACK to change your entry, or SELECT OK to save and continue. | [7 empty] | ${coagulantDose} >= 50 |  |  |  | valor de DOSIS DE COAGULANTES que ha entrado cae fuera del rango esperado (0.0-50.0). Por favor, VOLVER para cambiar el dato, o SELECCIONAR OK para guardarlo y seguir.
decimal | chlorineDose | Chlorine Dose (mg/L) |  |  |  |  | yes | [6 empty] | Dosis de cloro (mg/L)
decimal | entranceWaterLevel1 | Water level in the filter 1 entrance box (cm) |  |  |  |  | yes |  |  | ${nFilters} > 0 |  |  |  | Nivel de agua en la caja de entrada al filtro 1 (cm)
decimal | entranceWaterLevel2 | Water level in the filter 2 entrance box (cm) |  |  |  |  | yes |  |  | ${nFilters} > 1 |  |  |  | Nivel de agua en la caja de entrada al filtro 2 (cm)
decimal | entranceWaterLevel3 | Water level in the filter 3 entrance box (cm) |  |  |  |  | yes |  |  | ${nFilters} > 2 |  |  |  | Nivel de agua en la caja de entrada al filtro 3 (cm)
decimal | entranceWaterLevel4 | Water level in the filter 4 entrance box (cm) |  |  |  |  | yes |  |  | ${nFilters} > 3 |  |  |  | Nivel de agua en la caja de entrada al filtro 4 (cm)
decimal | entranceWaterLevel5 | Water level in the filter 5 entrance box (cm) |  |  |  |  | yes |  |  | ${nFilters} > 4 |  |  |  | Nivel de agua en la caja de entrada al filtro 5 (cm)
decimal | entranceWaterLevel6 | Water level in the filter 6 entrance box (cm) |  |  |  |  | yes |  |  | ${nFilters} > 5 |  |  |  | Nivel de agua en la caja de entrada al filtro 6 (cm)
select_one yes_no | backwashed | Do you need to report a backwash? | [7 empty] | ${nFilters} > 0 and not(selected(${purpose}, 'backwash')) |  |  |  | Usted necesita reportar un retrolavado?
end group
begin group | backwash | [8 empty] | selected(${purpose}, 'backwash') or ${backwashed} = 'yes'
calculate | filterList | [10 empty] | concat(${nFilters}, '_filters')
select_multiple filters | whichFilters | Which filters did you backwash? | [5 empty] | search('filterLists', contains, 'query', ${nFilters}) |  | ${nFilters} >= 2 |  |  |  | Con cuál(es) filtro(s) realizó el retrolavado?
datetime | backwashTime1 | When did you put filter 1 back online following the backwash? |  | We want to know when the backwash finished. | [5 empty] | selected(${whichFilters}, '1') |  |  | Queremos saber cuándo terminó el retrolavado. | Cuándo puso el filtro 1 en línea después del retrolavado?
decimal | backwashDuration1 | How long did the backwash last? (mins) |  |  | . <=60 and .>=5 | The BACKWASH DURATION you have entered is outside the expected range (5.0-60.0). |  |  |  | selected(${whichFilters}, '1') |  |  |  | Cuánto tiempo duró el retrolavado? (min)
datetime | backwashTime2 | When did you put filter 2 back online following the backwash? |  | We want to know when the backwash finished. | [5 empty] | selected(${whichFilters}, '2') |  |  | Queremos saber cuándo terminó el retrolavado. | Cuándo puso el filtro 2 en línea después del retrolavado?
decimal | backwashDuration2 | How long did the backwash last? (mins) |  |  | . <=60 and .>=5 | The BACKWASH DURATION you have entered is outside the expected range (5.0-60.0). |  |  |  | selected(${whichFilters}, '2') |  |  |  | Cuánto tiempo duró el retrolavado? (min)
datetime | backwashTime3 | When did you put filter 3 back online following the backwash? |  | We want to know when the backwash finished. | [5 empty] | selected(${whichFilters}, '3') |  |  | Queremos saber cuándo terminó el retrolavado. | Cuándo puso el filtro 3 en línea después del retrolavado?
decimal | backwashDuration3 | How long did the backwash last? (mins) |  |  | . <=60 and .>=5 | The BACKWASH DURATION you have entered is outside the expected range (5.0-60.0). |  |  |  | selected(${whichFilters}, '3') |  |  |  | Cuánto tiempo duró el retrolavado? (min)
datetime | backwashTime4 | When did you put filter 4 back online following the backwash? |  | We want to know when the backwash finished. | [5 empty] | selected(${whichFilters}, '4') |  |  | Queremos saber cuándo terminó el retrolavado. | Cuándo puso el filtro 4 en línea después del retrolavado?
decimal | backwashDuration4 | How long did the backwash last? (mins) |  |  | . <=60 and .>=5 | The BACKWASH DURATION you have entered is outside the expected range (5.0-60.0). |  |  |  | selected(${whichFilters}, '4') |  |  |  | Cuánto tiempo duró el retrolavado? (min)
datetime | backwashTime5 | When did you put filter 5 back online following the backwash? |  | We want to know when the backwash finished. | [5 empty] | selected(${whichFilters}, '5') |  |  | Queremos saber cuándo terminó el retrolavado. | Cuándo puso el filtro 5 en línea después del retrolavado?
decimal | backwashDuration5 | How long did the backwash last? (mins) |  |  | . <=60 and .>=5 | The BACKWASH DURATION you have entered is outside the expected range (5.0-60.0). |  |  |  | selected(${whichFilters}, '5') |  |  |  | Cuánto tiempo duró el retrolavado? (min)
datetime | backwashTime6 | When did you put filter 6 back online following the backwash? |  | We want to know when the backwash finished. | [5 empty] | selected(${whichFilters}, '6') |  |  | Queremos saber cuándo terminó el retrolavado. | Cuándo puso el filtro 6 en línea después del retrolavado?
decimal | backwashDuration6 | How long did the backwash last? (mins) |  |  | . <=60 and .>=5 | The BACKWASH DURATION you have entered is outside the expected range (5.0-60.0). |  |  |  | selected(${whichFilters}, '6') |  |  |  | Cuánto tiempo duró el retrolavado? (min)
end group
begin group | maintenanceDone | Maintenance Done | [7 empty] | ${purpose} = 'maintenanceDone' |  |  |  | Mantenimientos Hechos
string | repairsDoneOther | Tell us about the maintenance you did. | [11 empty] | Nos cuente del mantenimiento que hizo.
end group
begin group | maintenanceTODO | Maintenance To Do | [7 empty] | ${purpose} = 'maintenanceTODO' |  |  |  | Mantenimientos Para Hacer
string | ToDoDescription | What maintenance needs to be done? | [11 empty] | Qué mantenimiento hay que hacer?
end group
string | comments | Comments (optional) | [11 empty] | Comentarios (Opcional)
end group

## choices
list name | name | label | label::spanish
yes_no | yes | Yes
yes_no | no | No
plants | Ojojona | Ojojona
plants | Tamara | Tamara
plants | Marcala | Marcala
plants | Cuatro Comunidades | Cuatro Comunidades
plants | Agalteca | Agalteca
plants | Alauca | Alauca
plants | Atima | Atima
plants | San Nicolas | San Nicolas
plants | Moroceli | Moroceli
plants | Otoro | Otoro
plants | Matias | Matias
plants | Las Vegas | Las Vegas
purposes | plantData | Report plant data | Reportar datos sobre la planta
purposes | backwash | Report a backwash | Reportar un retrolavado
purposes | maintenanceDone | Report performed maintenance | Reportar mantenimiento realizado
purposes | maintenanceTODO | Report maintenance that needs to be done | Reportar mantenimiento que hay que hacer
purposes | Other | Other | Otra
filters | filter_name | filter_label